## Introduction
SF6 Alternatives Benefits Calculator
Vacuum Circuit Breaker (VCB) vs. SF6 Gas Circuit Breaker (GCB)
The U.S. Environmental Protection Agency developed the SF6 Alternatives Benefits Calculator to help evaluate the total lifetime cost of different
circuit breaker technologies. Specifically, users can compare the estimated costs of 72.5 kV and up SF₆-free vacuum breaker to an SF₆ gas insulated circuit
breaker of similar voltage and amp ratings. Users will need to gather O&M and capital cost information for each breaker. Once all cost information
has been gathered, users should start on "0. Assumptions" tab and fill out steps 0-5 of the calculator with the appropriate values to calculate the total
cost of one representative breaker over its lifetime. Sub-steps can be skipped or modified to accommodate the practices of the user.
The results show the discounted and undiscounted total and average annual costs for all breakers evaluated. The discounted cost provides a dollar value over the
lifetime of breakers that incorporates the decreasing value of money over time as opposed to the undiscounted rate which holds the value of money constant across the lifetime.
The tool includes the following user screens. To navigate to each screen, click on the arrows below.
Legend:
White boxes indicate input fields that require information from the user.
Gray boxes indicate calculated cells that are not editable.
Hatchmarked boxes indicate locked cells that are not editable.
Acknowledgements:
This tool was based off a model developed by Hitachi T&D Solutions, Inc. Components of the tool created by Hitachi and/or derived from Hitachi’s model
are used with Hitachi’s permission. EPA adapted this tool to add calculations of greenhouse gas emission reductions.
EPA thanks Hitachi T&D Solutions, Inc. for their support in the initial development of this tool, as well as Seattle City Light, Southern Company, Electric Utility Industry
Sustainable Supply Chain Alliance, MEPPI, GE Grid Solutions, and Siemens for reviewing the draft and providing feedback.
Disclaimer:
This calculator uses publicly available information in combination with information obtained through direct contact with electric utilities and other
stakeholders. EPA does not:
(a) make any warranty or representation, expressed or implied, with respect to the accuracy, completeness, or usefulness of the information contained
in this tool, or that the use of any apparatus, method, or process disclosed in this tool may not infringe upon privately owned rights;
(b) assume any liability with respect to the use of, or damages resulting from the use of, any information, apparatus, method, or process disclosed in
this tool; or
(c) imply endorsement of any technology supplier, product, or process mentioned in this tool.
This calculator was developed for U.S. EPA by ICF to estimate the cost comparison and greenhouse gas savings between vacuum circuit
breakers and SF6 gas insulated breakers. Actual costs and greenhouse gas savings may vary based on maintenance and other factors.
For questions or comment, please contact the Partnership at sf6partnership@epa.gov.
Definitions/Acronyms
Annual Cost
Initial Cost
Routine Inspection
Periodic Inspection
Replacement Cost
RESULTS
Assumptions

## Definitions and Acronyms
Definitions and Acronyms
Useful terminology presented throughout the tool
Definitions
0. Assumptions
Discount Rate - the interest rate used to find the present value of a product or service. Discounting renders benefits and costs that occur in different time periods comparable by
expressing their values in present terms. This allows the user to understand the actual cost that will be incurred for the breaker over its lifetime of service.
A lower discount rate values costs in the future more, while a higher discount rate values costs in the future less.
Lifetime - the time span from when a product is purchased to when it is decommissioned.
Routine Inspections - inspection of breakers done approximately every 6 to 15 years. The tool is set up to allow for the user to select any value.
Periodic Inspections - inspection of breakers done approximately every 18 to 30 years. The tool is set up to allow for the user to select any value.
Emissions Rate - the rate at which fugitive SF6 gas escapes from the circuit breaker and during handling.
SF₆ Nameplate Capacity per Breaker - the average charge of SF₆ breakers that are being evaluated in the tool.
1. Initial Cost per breaker
Tank Heater - heater used to keep breakers operational in extremely cold conditions.
Capital Cost - a onetime cost associated with the purchase of the breaker.
Installation Fee - costs associated with installing the new breaker into system. This should include any substation construction costs (labor and materials).
Other - Include any other costs not covered by aforementioned steps.
2. Annual Cost per breaker
Labor - hours of work performed by personnel or subcontractors on operations in breaker installation or maintenance
Annual Cost - costs associated with maintaining a breaker, averaged over each year. Equipment costs should be annualized.
Emissions Data Report - collecting, compiling and preparing SF₆ emissions report. Includes any EPA, local, internal, or voluntary reports.
Emissions Leak Check - routine labor needed to check for leaks.
Gas/SF₆ Purity Check - test needed to ensure the purity of the gas is high enough to maintain the dielectric properties.
Gas Storage/Handling - cost of storing and handling dry air or SF₆ in a year.
Gas/SF₆ Training - cost of training workers to properly handle dry gas or SF₆ without incident.
Site Hazardous Material Handling - cost of handling dry gas or SF₆ on site.
Gas/SF₆ Leak Repair - average cost of leak repairs needed at circuit breakers annually.
Electricity Cost: Space Heaters - cost to run space heaters for SF₆ insulated breakers.
Electricity Cost: Tank Heaters - cost to run tank heaters for SF₆ insulated breakers.
Dry Air Container - cost of secure container holding dry air on site.
Purity Meter - cost of buying/replacing instruments to ensure gas or SF₆ purity level.
SF₆ Gas Cylinders - total cost of all SF₆ gas purchased annually for the breakers being evaluated.
PPE & other cleaning materials - personal protective equipment such as respiratory device, rubber gloves, footwear, goggles), vacuum cleaner equipment (HEPA filters), wipes, waste
bags, hazardous waste drum for removal/handling of solid SF₆ byproducts.
SF₆ Repair Equip - materials required to repair SF₆ equipment such as desiccant, gaskets, clamps, valves, couplings.
3. Routine Inspection/ 4. Periodic Inspection per breaker
Routine Inspection - inspection that occurs on average every 6 to 15 years.
Periodic Inspection - inspection that occurs on average every 18 to 30 years.
Special note on Materials - if equipment or material is used for both periodic and routine inspection, users should input the costs of the equipment or material once, using either the
periodic or routine inspection step in the calculator, to avoid double counting of those costs.
Timing Test - test done to compare the circuit breaker's current contact performance with the ideal performance numbers provided by the manufacturer.
Taking out breaker for servicing - costs associated with the planning, reconfiguration, and safety measures in taking a breaker off-line for servicing.
Ductor Test - test measuring the resistance of electrical connections, usually at least 100A
Insulation Test - test that measurers the electrical insulation to ensure products can withstand high voltage; can include high voltage insulation test, control withstand test, and
vacuum bottle integrity test.
Visual Inspection - monthly spot check to ensure products are operating up to standard, also known as a Patrolling check.
Hi Pot Test - high potential (voltage) test to measures the electrical insulation to ensure products can withstand high voltage. Cost associated with Hi Pot Test should include any
additional costs related to safety.
Gas /SF₆ Analysis - test analyzing the quantity and purity of the gas or SF₆ in the circuit breaker.
Timing Analyzer - device needed to conduct a timing test accurately.
Ductor - equipment needed to measure low resistance levels, down to the micro-ohm.
Gas Removal - removing of gas from breaker during inspection
Contact Inspection - checking of electrical connections and resistance of breaker
Vacuum interrupter tester - testing kit, such as VIDAR, that checks the integrity of the vacuum interrupter.
Standard meters - meters measuring voltage
Vacuum/gas cart - cart used to evacuate gas from breakers
SF₆ gas meter - measures quantity of SF₆ gas from and to the breaker
5. Replacement or Overhaul Cost per breaker
Gas Recovery Cost and Reuse Offset - the net cost of gas recovery , i.e., the cost associated with sending gas off-site (for recycling/reclaiming/destruction) adjusted to account for
any credit received for selling reclaimed gas back into the supply chain
Decommissioning Cost - cost to dismantle and properly dispose of breaker and its parts.
RESULTS
Catastrophic Failure and Major Loss Events - unforeseen and unpredictable events that would lead to fugitive emissions of SF₆ gas into the atmosphere.
Undiscounted Total Cost - entire cost of the system over all the breakers' lifetime not accounting for the time value of money.
Average Annual Undiscounted Cost - yearly cost of the system based on the breakers' lifetime not accounting for the time value of money.
Discounted Total Cost - entire cost of the system over all the breakers' lifetime accounting for the time value of money.
Average Annual Discounted Cost - yearly cost of the system based on the breaker's lifetime accounting for the time value of money.
Acronyms
GCB | Gas Circuit Breaker
Hi Pot | High Potential
kV | Kilovolt
kWh | kilowatt-hour
MTCO₂e | Metric Tons of CO₂ Equivalent
PPE | Personal Protective Equipment
SF₆ | Sulfur Hexafluoride
VCB | Vacuum Circuit Breaker

## 0. Assumptions
Assumptions: |  | (hide these columns)
On this page, you are setting up the scenario that you want to evaluate.
For additional information on definitions and acronyms used, please refer to "Definitions and Acronyms" tab |  | # | freq RI - VCB | freq RI - GCB | freq PI - VCB | freq PI - GCB | discount rate
Calculated Cell | Input Cell | 1 | 10 | 10 | 14 | 5 | 3%
|  | 2 | 20 | 20 | 28 | 10 | 5%
General |  | 3 | 30 | 30 | 42 | 15 | 7%
Assumption | Value | 4 | 40 | 40 | 56 | 20
Discount Rate | 3% | 5 | 50 | 50 | 70 | 25
Number of breakers to evaluate | 4 | 6 | 60 | 60 | 84 | 30
|  | 7 | 70 | 70 | 98 | 35
VCB |  | 8 | 80 | 80 | 112 | 40
Assumption | Value | 9 | 90 | 90 | 126 | 45
Number of VCB in system | 4 | 10 | 100 | 100 | 140 | 50
Lifetime of VCB | 40 | 11 | 110 | 110 | 154 | 55
Average number of routine inspections per lifetime | 4 | 12 | 120 | 120 | 168 | 60
Average number of periodic inspections per lifetime | 3 | 13 | 130 | 130 | 182 | 65
Interval in which routine inspections take place (years) | 10 | 14 | 140 | 140 | 196 | 70
Interval in which periodic inspections take place (years) | 14 | 15 | 150 | 150 | 210 | 75
|  | 16 | 160 | 160 | 224 | 80
GCB |  | 17 | 170 | 170 | 238 | 85
Assumption | Value | 18 | 180 | 180 | 252 | 90
Number of GCB in system | 4 | 19 | 190 | 190 | 266 | 95
Lifetime of GCB | 40 | 20 | 200 | 200 | 280 | 100
Average number of routine inspections per lifetime | 4 | 21 | 210 | 210 | 294 | 105
Average number of periodic inspections per lifetime | 8 | 22 | 220 | 220 | 308 | 110
Interval in which routine inspections take place (years) | 10 | 23 | 230 | 230 | 322 | 115
Interval in which periodic inspections take place (years) | 5 | 24 | 240 | 240 | 336 | 120
|  | 25 | 250 | 250 | 350 | 125
Environmental Benefits |  | 26 | 260 | 260 | 364 | 130
Assumption | Value | 27 | 270 | 270 | 378 | 135
SF₆ Emission rate of utility (pounds emissions of SF₆ per nameplate capacity) | 0.5% | 28 | 280 | 280 | 392 | 140
SF₆ nameplate capacity per breaker (pounds) | 80 | 29 | 290 | 290 | 406 | 145
|  | 30 | 300 | 300 | 420 | 150
|  | 31 | 310 | 310 | 434 | 155
|  | 32 | 320 | 320 | 448 | 160
|  | 33 | 330 | 330 | 462 | 165
|  | 34 | 340 | 340 | 476 | 170
|  | 35 | 350 | 350 | 490 | 175
|  | 36 | 360 | 360 | 504 | 180
|  | 37 | 370 | 370 | 518 | 185
|  | 38 | 380 | 380 | 532 | 190
|  | 39 | 390 | 390 | 546 | 195
|  | 40 | 400 | 400 | 560 | 200
|  | 41 | 410 | 410 | 574 | 205
|  | 42 | 420 | 420 | 588 | 210
|  | 43 | 430 | 430 | 602 | 215
|  | 44 | 440 | 440 | 616 | 220
|  | 45 | 450 | 450 | 630 | 225
|  | 46 | 460 | 460 | 644 | 230
|  | 47 | 470 | 470 | 658 | 235
|  | 48 | 480 | 480 | 672 | 240
|  | 49 | 490 | 490 | 686 | 245
|  | 50 | 500 | 500 | 700 | 250
|  | 51 | 510 | 510 | 714 | 255
|  | 52 | 520 | 520 | 728 | 260
|  | 53 | 530 | 530 | 742 | 265
|  | 54 | 540 | 540 | 756 | 270
|  | 55 | 550 | 550 | 770 | 275
|  | 56 | 560 | 560 | 784 | 280
|  | 57 | 570 | 570 | 798 | 285
|  | 58 | 580 | 580 | 812 | 290
|  | 59 | 590 | 590 | 826 | 295
|  | 60 | 600 | 600 | 840 | 300

## 1. Initial Cost
Total Ownership Cost Analysis Vacuum Circuit Breaker (VCB) vs. SF₆ Gas Circuit Breaker (GCB)
For additional information on definitions and acronyms used, please refer to "Definitions and Acronyms" tab
Calculated Cell | Input Cell | Not Applicable
1. Initial Cost:
VCB
| Labor |  |  | Materials
Item Description | Labor Hours | $/hr. | Cost of Labor Hours | Equipment Needed | Cost of Equipment | Category Cost
Capital Costs |  |  | 0 | Breaker | 788000 | 788000
Installation Fee | 400 | 125 | 50000 | Servicing Materials | 5000 | 55000
Other |  |  | 0 |  |  | 0
Total Initial Cost | [5 empty] | 843000
SF₆ GCB
| Labor |  |  | Materials
Item Description | Labor Hours | $/hr. | Cost of Labor Hours | Equipment Needed | Cost of Equipment | Category Cost
Capital Costs |  |  | 0 | Breaker | 352000 | 352000
Installation Fee | 400 | 125 | 50000 | Servicing Materials | 5000 | 55000
Other |  |  | 0 |  |  | 0
Total Initial Cost | [5 empty] | 407000
SF₆ GCB with Tank Heater
| Labor |  |  | Materials
Item Description | Labor Hours | $/hr. | Cost of Labor Hours | Equipment Needed | Cost of Equipment | Category Cost
Capital Costs |  |  | 0 | Breaker | 352000 | 352000
Installation Fee | 400 | 125 | 50000 | Servicing Materials | 5000 | 55000
Other |  |  | 0 |  |  | 0
Total Initial Cost | [5 empty] | 407000

## 2. Annual Cost
Total Ownership Cost Analysis Vacuum Circuit Breaker (VCB) vs. SF₆ Gas Circuit Breaker (GCB)
For additional information on definitions and acronyms used, please refer to "Definitions and Acronyms" tab
Calculated Cell | Input Cell | Not Applicable
2. Annual Cost:
VCB
| Labor |  |  | Materials
Item Description | Labor Hours per Year | $/hr. | Cost of Labor Hours/Year | Equipment Needed | Cost of Equipment per year | Category Cost
Emission Data Report | 10 | 125 | 1250 | Not Applicable |  | 1250
Emissions Leak Check |  |  | 0 | Not Applicable |  | 0
Gas Purity Check |  |  | 0 | Not Applicable |  | 0
Gas Storage/Handling |  |  | 0 | Dry Air Container | 1500 | 1500
Gas Training |  |  | 0 | Not Applicable |  | 0
Site Hazardous Material Handling |  |  | 0 | Not Applicable |  | 0
Gas Leak Repair |  |  | 0 | Not Applicable |  | 0
Other |  |  | 0 |  |  | 0
Cabinet/Tank Heater Operations-Hrs. |  |  | Hours | kW required | $/kWh | Total Annual Category Cost per VCB
Electricity Cost - Space Heaters | [5 empty] | 0
Electricity Cost - Tank Heaters | [5 empty] | 0
Total Annual Cost | [5 empty] | 2750
SF₆ GCB
| Labor |  |  | Materials
Item Description | Labor Hours per Year | $/hr. | Cost of Labor Hours/Year | Equipment Needed | Cost of Equipment per year | Category Cost
SF₆ Emission Data Report | 40 | 125 | 5000 | Not Applicable |  | 5000
SF₆ Emission Data Collection/Leak Check |  |  | 0 | Leak Detection Equipment |  | 0
SF₆ Purity Check | 10 | 125 | 1250 | Purity Meter | 6500 | 7750
SF₆ Gas Storage/Handling |  |  | 0 | SF₆ Gas Cylinders | 1500 | 1500
SF₆ Training |  |  | 0 | Not Applicable |  | 0
Site Hazardous Material Handling |  |  | 0 | PPE & other cleaning materials |  | 0
SF₆ Leak Repair | 40 | 125 | 5000 | SF₆ Repair Equip |  | 5000
Other |  |  | 0 |  |  | 0
Cabinet/Tank Heater Operations-Hrs. |  |  | Hours | kW required | $/kWh | Total Annual Category Cost per GCB
Electricity Cost - Space Heaters |  |  | 2190 | 0.19 | 0.18 | 74.898
Electricity Cost - Tank Heaters |  |  | 2190 | 3 | 0.18 | 1182.6
Total Annual Cost | [5 empty] | 20507.498

## 3. Routine Inspection
Total Ownership Cost Analysis Vacuum Circuit Breaker (VCB) vs. SF₆ Gas Circuit Breaker (GCB)
For additional information on definitions and acronyms used, please refer to "Definitions and Acronyms" tab
Calculated Cell | Input Cell | Not Applicable
3. Routine Inspection:
VCB
| Labor |  |  | Materials
Item Description | Labor hour | $/hr. | Cost of Labor | Equipment Needed | Cost of Equipment | Total Cost
Timing Test |  |  | 0 | Timing Analyzer |  | 0
Taking out breaker for servicing |  |  | 0 | Not Applicable |  | 0
Ductor Test |  |  | 0 | Ductor |  | 0
Insulation Test |  |  | 0 | Vacuum interrupter tester |  | 0
Visual Inspection |  |  | 0 | Standard meters |  | 0
Hi Pot Test |  |  | 0 | Hi Pot |  | 0
Gas Analysis | 10 | 125 | 1250 | Not Applicable |  | 1250
Other |  |  | 0 |  |  | 0
Total Routine Inspection | [5 empty] | 1250
SF₆ GCB
| Labor |  |  | Materials
Item Description | Labor hour | $/hr. | Cost of Labor | Equipment Needed | Cost of Equipment | Total Cost per GCB
Timing Test |  |  | 0 | Timing Analyzer |  | 0
Taking out breaker for servicing |  |  | 0 | Not Applicable |  | 0
Ductor Test |  |  | 0 | Ductor |  | 0
Insulation Test |  |  | 0 | Vacuum interrupter tester |  | 0
Visual Inspection |  |  | 0 | Standard meters |  | 0
Hi Pot Test |  |  | 0 | Not Applicable |  | 0
SF₆ Analysis | 10 | 125 | 1250 | SF₆ gas meter |  | 1250
Other |  |  | 0 |  |  | 0
Total Routine Inspection | [5 empty] | 1250

## 4. Periodic Inspection
Total Ownership Cost Analysis Vacuum Circuit Breaker (VCB) vs. SF₆ Gas Circuit Breaker (GCB)
For additional information on definitions and acronyms used, please refer to "Definitions and Acronyms" tab
Calculated Cell | Input Cell | Not Applicable
4. Periodic Inspection:
VCB
| Labor |  |  | Materials
Item Description | Labor hour | $/hr. | Cost of Labor | Equipment Needed | Cost of Equipment | Total Cost
Timing Test | 10 | 125 | 1250 | Timing Analyzer |  | 1250
Taking out breaker for servicing |  |  | 0 | Not Applicable |  | 0
Ductor Test | 40 | 125 | 5000 | Ductor |  | 5000
Insulation Test |  |  | 0 | Vacuum interrupter tester |  | 0
Visual Inspection |  |  | 0 | Standard meters |  | 0
Hi Pot Test |  |  | 0 | Hi Pot |  | 0
Gas Analysis |  |  | 0 | Not Applicable |  | 0
Gas Removal |  |  | 0 | Vacuum cart |  | 0
Contact Inspection |  |  | 0 | Not Applicable |  | 0
18 year maintenance parts |  |  | 0 | Parts |  | 0
Other |  |  | 0 |  |  | 0
Total Periodic Inspection | [5 empty] | 6250
SF₆ GCB
| Labor |  |  | Materials
Item Description | Labor hour | $/hr. | Cost of Labor | Equipment Needed | Cost of Equipment | Total Cost per GCB
Timing Test | 10 | 125 | 1250 | Timing Analyzer |  | 1250
Taking out breaker for servicing |  |  | 0 | Not Applicable |  | 0
Ductor Test | 40 | 125 | 5000 | Ductor |  | 5000
Insulation Test |  |  | 0 | Vacuum interrupter tester |  | 0
Visual Inspection |  |  | 0 | Standard meters |  | 0
Hi Pot Test |  |  | 0 | Not Applicable |  | 0
SF₆ Analysis |  |  | 0 | SF₆ gas meter |  | 0
Gas Removal |  |  | 0 | Gas cart |  | 0
Contact Inspection | 40 | 125 | 5000 | Not Applicable |  | 5000
18 year maintenance parts |  |  | 0 | Parts |  | 0
Other |  |  | 0 |  |  | 0
Total Periodic Inspection | [5 empty] | 11250

## 5. Replacement or Overhaul Cost
Total Ownership Cost Analysis Vacuum Circuit Breaker (VCB) vs. SF₆ Gas Circuit Breaker (GCB)
For additional information on definitions and acronyms used, please refer to "Definitions and Acronyms" tab
Calculated Cell | Input Cell
5. Breaker Replacement/Overhaul Cost:
Items Description | VCB
Gas Recovery Cost and Reuse Offset | 0
Decommissioning Cost | 10000
Other
Total Breaker Replacement/Overhaul Cost | 10000
Items Description | SF₆ GCB no Tank Heater
Gas Recovery Cost and Reuse Offset
Decommissioning Cost | 10000
Other
Total Breaker Replacement/Overhaul Cost | 10000
Items Description | SF₆ GCB with Tank Heater
Gas Recovery Cost and Reuse Offset | 10000
Decommissioning Cost | 10000
Other
Total Breaker Replacement/Overhaul Cost | 20000

## RESULTS
Results
By choosing 4 VCBs, your utility could save an estimated $3,331 over the life of the breakers as compared to the most expensive option of the SF6 GCB with Tank Heater.
Your utility will prevent an estimated 682 metric tons of CO₂ equivalent (MTCO₂e) of SF₆ emissions over the breaker lifetime, based on an emission rate of 0.5%.*
Your emissions savings is equivalent to removing approximately 152 passenger vehicles driven for one year.*
Potential emissions avoided in a given year can be as high as 3,309 MTCO₂e when considering the total SF₆ capacity and the potential for catastrophic failure and major loss events.
Greenhouse Gas Savings
Estimated SF6 savings over breaker lifetime
Emissions Savings | Pounds of SF6 | MTCO2e* | Equivalency of Passenger Vehicles Driven per Year
Per breaker | 16 | 170.5536 | 37.9852
Total breakers evaluated | 64 | 682.2144 | 151.9408
Total Ownership Cost Comparison
Estimated cost comparison over breaker lifetime
Cost Savings | VCB | SF6 GCB no Tank Heater | SF6 GCB with Tank Heater
Undiscounted Total Cost | 3947000 | 5329199.68 | 5369199.68
Average Annual Undiscounted Cost | 98675 | 133229.992 | 134229.992
Discounted Total Cost | 3685183.0315 | 3805799.2292 | 3818429.371
Average Annual Discounted Cost | 92129.5758 | 95144.9807 | 95460.7343
Most cost effective option: | VCB
Based on average annual discounted cost
Cost Savings from Avoided SF6 Gas Purchases
Estimated costs saved from avoided SF6 gas purchases
Cost Savings
Per breaker | 15000
Total breakers evaluated | 60000
Summary Charts
* Source: Greenhouse Gases Equivalencies Calculator - Calculations and References, Last Updated October 2023
Available online at
https://www.epa.gov/energy/greenhouse-gases-equivalencies-calculator-calculations-and-references
GWP of SF₆: 23,500. Source: IPCC's Fifth Assessment Report, 2014 (AR5)

## NPV Analysis (hidden)
| VCB | [6 empty] | SF6 GCB no Tank Heater | [6 empty] | SF6 GCB with Tank Heater
(hide) | Year | Initial Costs | Annual Costs | Routine Inspection | Periodic Inspections | Breaker Replacement/ Overhaul Costs | Total | Year | Initial Costs | Annual Costs | Routine Inspection | Periodic Inspections | Breaker Replacement/ Overhaul Costs | Total | Year | Initial Costs | Annual Costs | Routine Inspection | Periodic Inspections | Breaker Replacement/ Overhaul Costs | Total | Year | VCB | SF6 GCB with no Tank Heater | SF6 GCB with Tank Heater
1 | 1 | 3372000 | 11000 | 0 | 0 | 0 | 3383000 | 1 | 1628000 | 82029.992 | 0 | 0 | 0 | 1710029.992 | 1 | 1628000 | 82029.992 | 0 | 0 | 0 | 1710029.992 | 1 | 3383000 | 1710029.992 | 1710029.992
2 | 2 |  | 10679.6117 | 0 | 0 | 0 | 10679.6117 | 2 |  | 79640.7689 | 0 | 0 | 0 | 79640.7689 | 2 |  | 79640.7689 | 0 | 0 | 0 | 79640.7689 | 2 | 3393679.6117 | 1789670.7609 | 1789670.7609
3 | 3 |  | 10368.555 | 0 | 0 | 0 | 10368.555 | 3 |  | 77321.1349 | 0 | 0 | 0 | 77321.1349 | 3 |  | 77321.1349 | 0 | 0 | 0 | 77321.1349 | 3 | 3404048.1667 | 1866991.8958 | 1866991.8958
4 | 4 |  | 10066.5583 | 0 | 0 | 0 | 10066.5583 | 4 |  | 75069.063 | 0 | 0 | 0 | 75069.063 | 4 |  | 75069.063 | 0 | 0 | 0 | 75069.063 | 4 | 3414114.7249 | 1942060.9588 | 1942060.9588
5 | 5 |  | 9773.3575 | 0 | 0 | 0 | 9773.3575 | 5 |  | 72882.5854 | 0 | 39981.9172 | 0 | 112864.5026 | 5 |  | 72882.5854 | 0 | 39981.9172 | 0 | 112864.5026 | 5 | 3423888.0824 | 2054925.4614 | 2054925.4614
6 | 6 |  | 9488.6966 | 0 | 0 | 0 | 9488.6966 | 6 |  | 70759.7917 | 0 | 0 | 0 | 70759.7917 | 6 |  | 70759.7917 | 0 | 0 | 0 | 70759.7917 | 6 | 3433376.7791 | 2125685.2531 | 2125685.2531
7 | 7 |  | 9212.3268 | 0 | 0 | 0 | 9212.3268 | 7 |  | 68698.8269 | 0 | 0 | 0 | 68698.8269 | 7 |  | 68698.8269 | 0 | 0 | 0 | 68698.8269 | 7 | 3442589.1059 | 2194384.08 | 2194384.08
8 | 8 |  | 8944.0066 | 0 | 0 | 0 | 8944.0066 | 8 |  | 66697.8902 | 0 | 0 | 0 | 66697.8902 | 8 |  | 66697.8902 | 0 | 0 | 0 | 66697.8902 | 8 | 3451533.1125 | 2261081.9701 | 2261081.9701
9 | 9 |  | 8683.5016 | 0 | 0 | 0 | 8683.5016 | 9 |  | 64755.2332 | 0 | 0 | 0 | 64755.2332 | 9 |  | 64755.2332 | 0 | 0 | 0 | 64755.2332 | 9 | 3460216.6141 | 2325837.2033 | 2325837.2033
10 | 10 |  | 8430.5841 | 3832.0837 | 0 | 0 | 12262.6677 | 10 |  | 62869.1584 | 3832.0837 | 34488.753 | 0 | 101189.995 | 10 |  | 62869.1584 | 3832.0837 | 34488.753 | 0 | 101189.995 | 10 | 3472479.2818 | 2427027.1983 | 2427027.1983
11 | 11 |  | 8185.0331 | 0 | 0 | 0 | 8185.0331 | 11 |  | 61038.0179 | 0 | 0 | 0 | 61038.0179 | 11 |  | 61038.0179 | 0 | 0 | 0 | 61038.0179 | 11 | 3480664.3149 | 2488065.2162 | 2488065.2162
12 | 12 |  | 7946.634 | 0 | 0 | 0 | 7946.634 | 12 |  | 59260.2115 | 0 | 0 | 0 | 59260.2115 | 12 |  | 59260.2115 | 0 | 0 | 0 | 59260.2115 | 12 | 3488610.9489 | 2547325.4278 | 2547325.4278
13 | 13 |  | 7715.1787 | 0 | 0 | 0 | 7715.1787 | 13 |  | 57534.186 | 0 | 0 | 0 | 57534.186 | 13 |  | 57534.186 | 0 | 0 | 0 | 57534.186 | 13 | 3496326.1276 | 2604859.6137 | 2604859.6137
14 | 14 |  | 7490.4647 | 0 | 17023.7835 | 0 | 24514.2482 | 14 |  | 55858.433 | 0 | 0 | 0 | 55858.433 | 14 |  | 55858.433 | 0 | 0 | 0 | 55858.433 | 14 | 3520840.3758 | 2660718.0467 | 2660718.0467
15 | 15 |  | 7272.2959 | 0 | 0 | 0 | 7272.2959 | 15 |  | 54231.4883 | 0 | 29750.3013 | 0 | 83981.7896 | 15 |  | 54231.4883 | 0 | 29750.3013 | 0 | 83981.7896 | 15 | 3528112.6717 | 2744699.8363 | 2744699.8363
16 | 16 |  | 7060.4814 | 0 | 0 | 0 | 7060.4814 | 16 |  | 52651.9304 | 0 | 0 | 0 | 52651.9304 | 16 |  | 52651.9304 | 0 | 0 | 0 | 52651.9304 | 16 | 3535173.1531 | 2797351.7667 | 2797351.7667
17 | 17 |  | 6854.8363 | 0 | 0 | 0 | 6854.8363 | 17 |  | 51118.379 | 0 | 0 | 0 | 51118.379 | 17 |  | 51118.379 | 0 | 0 | 0 | 51118.379 | 17 | 3542027.9894 | 2848470.1457 | 2848470.1457
18 | 18 |  | 6655.1809 | 0 | 0 | 0 | 6655.1809 | 18 |  | 49629.4942 | 0 | 0 | 0 | 49629.4942 | 18 |  | 49629.4942 | 0 | 0 | 0 | 49629.4942 | 18 | 3548683.1704 | 2898099.64 | 2898099.64
19 | 19 |  | 6461.3407 | 0 | 0 | 0 | 6461.3407 | 19 |  | 48183.975 | 0 | 0 | 0 | 48183.975 | 19 |  | 48183.975 | 0 | 0 | 0 | 48183.975 | 19 | 3555144.511 | 2946283.6149 | 2946283.6149
20 | 20 |  | 6273.1463 | 2851.4301 | 0 | 0 | 9124.5764 | 20 |  | 46780.5582 | 2851.4301 | 25662.8712 | 0 | 75294.8596 | 20 |  | 46780.5582 | 2851.4301 | 25662.8712 | 0 | 75294.8596 | 20 | 3564269.0875 | 3021578.4745 | 3021578.4745
21 | 21 |  | 6090.4333 | 0 | 0 | 0 | 6090.4333 | 21 |  | 45418.0177 | 0 | 0 | 0 | 45418.0177 | 21 |  | 45418.0177 | 0 | 0 | 0 | 45418.0177 | 21 | 3570359.5208 | 3066996.4922 | 3066996.4922
22 | 22 |  | 5913.042 | 0 | 0 | 0 | 5913.042 | 22 |  | 44095.1628 | 0 | 0 | 0 | 44095.1628 | 22 |  | 44095.1628 | 0 | 0 | 0 | 44095.1628 | 22 | 3576272.5628 | 3111091.655 | 3111091.655
23 | 23 |  | 5740.8175 | 0 | 0 | 0 | 5740.8175 | 23 |  | 42810.8377 | 0 | 0 | 0 | 42810.8377 | 23 |  | 42810.8377 | 0 | 0 | 0 | 42810.8377 | 23 | 3582013.3803 | 3153902.4926 | 3153902.4926
24 | 24 |  | 5573.6092 | 0 | 0 | 0 | 5573.6092 | 24 |  | 41563.9201 | 0 | 0 | 0 | 41563.9201 | 24 |  | 41563.9201 | 0 | 0 | 0 | 41563.9201 | 24 | 3587586.9895 | 3195466.4127 | 3195466.4127
25 | 25 |  | 5411.2711 | 0 | 0 | 0 | 5411.2711 | 25 |  | 40353.3205 | 0 | 22137.0181 | 0 | 62490.3386 | 25 |  | 40353.3205 | 0 | 22137.0181 | 0 | 62490.3386 | 25 | 3592998.2606 | 3257956.7513 | 3257956.7513
26 | 26 |  | 5253.6613 | 0 | 0 | 0 | 5253.6613 | 26 |  | 39177.981 | 0 | 0 | 0 | 39177.981 | 26 |  | 39177.981 | 0 | 0 | 0 | 39177.981 | 26 | 3598251.9219 | 3297134.7323 | 3297134.7323
27 | 27 |  | 5100.642 | 0 | 0 | 0 | 5100.642 | 27 |  | 38036.8748 | 0 | 0 | 0 | 38036.8748 | 27 |  | 38036.8748 | 0 | 0 | 0 | 38036.8748 | 27 | 3603352.5639 | 3335171.6071 | 3335171.6071
28 | 28 |  | 4952.0796 | 0 | 11254.7264 | 0 | 16206.806 | 28 |  | 36929.0046 | 0 | 0 | 0 | 36929.0046 | 28 |  | 36929.0046 | 0 | 0 | 0 | 36929.0046 | 28 | 3619559.3699 | 3372100.6117 | 3372100.6117
29 | 29 |  | 4807.8443 | 0 | 0 | 0 | 4807.8443 | 29 |  | 35853.4026 | 0 | 0 | 0 | 35853.4026 | 29 |  | 35853.4026 | 0 | 0 | 0 | 35853.4026 | 29 | 3624367.2142 | 3407954.0143 | 3407954.0143
30 | 30 |  | 4667.81 | 2121.7318 | 0 | 0 | 6789.5418 | 30 |  | 34809.1287 | 2121.7318 | 19095.5863 | 0 | 56026.4468 | 30 |  | 34809.1287 | 2121.7318 | 19095.5863 | 0 | 56026.4468 | 30 | 3631156.756 | 3463980.4611 | 3463980.4611
31 | 31 |  | 4531.8544 | 0 | 0 | 0 | 4531.8544 | 31 |  | 33795.2706 | 0 | 0 | 0 | 33795.2706 | 31 |  | 33795.2706 | 0 | 0 | 0 | 33795.2706 | 31 | 3635688.6103 | 3497775.7317 | 3497775.7317
32 | 32 |  | 4399.8586 | 0 | 0 | 0 | 4399.8586 | 32 |  | 32810.9423 | 0 | 0 | 0 | 32810.9423 | 32 |  | 32810.9423 | 0 | 0 | 0 | 32810.9423 | 32 | 3640088.4689 | 3530586.674 | 3530586.674
33 | 33 |  | 4271.7074 | 0 | 0 | 0 | 4271.7074 | 33 |  | 31855.2838 | 0 | 0 | 0 | 31855.2838 | 33 |  | 31855.2838 | 0 | 0 | 0 | 31855.2838 | 33 | 3644360.1763 | 3562441.9578 | 3562441.9578
34 | 34 |  | 4147.2887 | 0 | 0 | 0 | 4147.2887 | 34 |  | 30927.46 | 0 | 0 | 0 | 30927.46 | 34 |  | 30927.46 | 0 | 0 | 0 | 30927.46 | 34 | 3648507.465 | 3593369.4178 | 3593369.4178
35 | 35 |  | 4026.4939 | 0 | 0 | 0 | 4026.4939 | 35 |  | 30026.6602 | 0 | 16472.0205 | 0 | 46498.6807 | 35 |  | 30026.6602 | 0 | 16472.0205 | 0 | 46498.6807 | 35 | 3652533.9589 | 3639868.0985 | 3639868.0985
36 | 36 |  | 3909.2174 | 0 | 0 | 0 | 3909.2174 | 36 |  | 29152.0973 | 0 | 0 | 0 | 29152.0973 | 36 |  | 29152.0973 | 0 | 0 | 0 | 29152.0973 | 36 | 3656443.1763 | 3669020.1958 | 3669020.1958
37 | 37 |  | 3795.3567 | 0 | 0 | 0 | 3795.3567 | 37 |  | 28303.0071 | 0 | 0 | 0 | 28303.0071 | 37 |  | 28303.0071 | 0 | 0 | 0 | 28303.0071 | 37 | 3660238.533 | 3697323.2029 | 3697323.2029
38 | 38 |  | 3684.8123 | 0 | 0 | 0 | 3684.8123 | 38 |  | 27478.6476 | 0 | 0 | 0 | 27478.6476 | 38 |  | 27478.6476 | 0 | 0 | 0 | 27478.6476 | 38 | 3663923.3453 | 3724801.8505 | 3724801.8505
39 | 39 |  | 3577.4877 | 0 | 0 | 0 | 3577.4877 | 39 |  | 26678.2987 | 0 | 0 | 0 | 26678.2987 | 39 |  | 26678.2987 | 0 | 0 | 0 | 26678.2987 | 39 | 3667500.833 | 3751480.1492 | 3751480.1492
40 | 40 |  | 3473.289 | 1578.7677 | 0 | 12630.1418 | 17682.1986 | 40 |  | 25901.2609 | 1578.7677 | 14208.9096 | 12630.1418 | 54319.08 | 40 |  | 25901.2609 | 1578.7677 | 14208.9096 | 25260.2837 | 66949.2218 | 40 | 3685183.0315 | 3805799.2292 | 3818429.371
41 |  |  | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | #N/A | #N/A | #N/A
42 |  |  | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | #N/A | #N/A | #N/A
43 |  |  | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | #N/A | #N/A | #N/A
44 |  |  | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | #N/A | #N/A | #N/A
45 |  |  | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | #N/A | #N/A | #N/A
46 |  |  | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | #N/A | #N/A | #N/A
47 |  |  | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | #N/A | #N/A | #N/A
48 |  |  | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | #N/A | #N/A | #N/A
49 |  |  | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | #N/A | #N/A | #N/A
50 |  |  | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | #N/A | #N/A | #N/A
| Total Cost | 3372000 | 261890.3665 | 10384.0133 | 28278.5099 | 12630.1418 | 3685183.0315 | Total Cost | 1628000 | 1952987.6969 | 10384.0133 | 201797.3771 | 12630.1418 | 3805799.2292 | Total Cost | 1628000 | 1952987.6969 | 10384.0133 | 201797.3771 | 25260.2837 | 3818429.371
| Annual Cost | 84300 | 6547.2592 | 259.6003 | 706.9627 | 315.7535 | 92129.5758 | Annual Cost | 40700 | 48824.6924 | 259.6003 | 5044.9344 | 315.7535 | 95144.9807 | Annual Cost | 40700 | 48824.6924 | 259.6003 | 5044.9344 | 631.5071 | 95460.7343

## Constants and Conversions (hidden)
Conversion Factors
SF6 Global Warming Potential | 23500
Short Tons to Metric Tons | 0.9072
Short Tons to Pounds | 2000
lbs to MT | 2204.5855
Passenger Vehicles Per year | 4.49
Note on B3: Carr, Emily: IPCC 5th Assessement Report
Note on B7: Vaingankar, Neha: https://www.epa.gov/energy/greenhouse-gases-equivalencies-calculator-calculations-and-references